## Sheet1
Template Category | Water Heater (Circulating) - Gas or Oil
Template Version | v1
Category Description | Gas or Oil Fired Circulating Water Heater used to produce hot water
Classification System
Classification | Value
Suitability for Use | Approved
Template Custodian | CIBSE
Information Category | Parameter Name | Value | Units | Notes
Manufacturer Data
Specifications | Manufacturer | Lochinvar Limited | Text
Specifications | Manufacturer Website | Lochinvar Ltd. UK ¦ High Efficiency Water Heaters and Boilers | URL
Specifications | Product Range | EcoKnight Water heaters | Text
Specifications | Product Model Number | EKW86 CE | Text | Or Code
Specifications | CE Approval | YES 0063CQ3351 | Text | Number, Yes, No
Specifications | Product Literature | http://lochinvar.ltd.uk/heater/ecoknight%E2%84%A2-water-heaters | URL
Specifications | Additional Technical Details |  | URL | URL to technical details, e.g. system flow rates, pressure drop curves
Specifications | Features | Floor standing condensing water heater | Text | Free text to describe product
Construction Data
Specifications | Type | Hot water generator | Enumeration
Specifications | Configuration | Cascade boilers | Enumeration
Specifications | Shape | Rectangular (Horizontal) | Enumeration
Specifications | External Material | Steel | Enumeration
Specifications | Colour | Light Grey | Text | e.g. RAL, Colour
Specifications | Finish | Painted | Text | e.g. Anodised, Brushed, Painted, Natural (Self-finish)
Specifications | Mounting | Floor Standing | Enumeration
Specifications | Burner Control Type | Modulating | Enumeration
Specifications | Heater Operation | Condensing | Enumeration | State whether product has condensing function
Specifications | Primary Heat Exchanger Material | Stainless Steel | Enumeration
Specifications | Secondary Heat Exchanger Material | No secondary heat exchanger | Enumeration | If Not Applicable, choose 'No secondary heat exchanger'
Specifications | Primary Shunt Description | Bronze glanded pump | Text | Free text to describe shunt pump details
Specifications | Buffer Vessel Description | Project specific | Text | Free text to describe buffer vessel details
Specifications | Fuel Connection Type | Threaded | Enumeration
Specifications | Flow and Return Connection Type | Threaded | Enumeration
Specifications | Drain Connection Type | Threaded | Enumeration
Specifications | Safety Valve Connection Type | Threaded | Enumeration
Specifications | Condensate Drain Type | Threaded | Enumeration
Specifications | Flue or Air Intake Classification | B23,C13,C33,C43,C53 | Text | Flue/air intake classification standard, e.g. 'B23'
Application Data
Specifications | Reference Standard | EN15420 | Text | BS, EN, ISO
Specifications | WRAS Approval | Yes 1407063 | Text | Number, Yes, No
Dimensional Data
Specifications | Overall Length | 502 | mm | Depth or Diameter
Specifications | Overall Width | 394 | mm
Specifications | Overall Height | 1080 | mm
Specifications | Gross Weight | 111.1 | kg | Equates to operating weight
Specifications | Water Content | 9.1 | litres
Specifications | Shipping Weight | 102 | kg | Equates to dry weight of unit plus packaging allowance
Specifications | Access Clearance Top | 330 | mm | Access required for maintenance of this item
Specifications | Access Clearance Bottom | 10 | mm | Access required for maintenance of this item
Specifications | Access Clearance Left | 400 | mm | Access required for maintenance of this item
Specifications | Access Clearance Right | 0 | mm | Access required for maintenance of this item
Specifications | Access Clearance Front | 460 | mm | Access required for maintenance of this item
Specifications | Access Clearance Rear | 360 | mm | Access required for maintenance of this item
Specifications | Fuel Connection Size | 3/4 | inches | Choose units from dropdown
Specifications | Flow and Return Connection Size | 2 | inches | Choose units from dropdown
Specifications | Drain Connection Size | 3/4 | inches | Choose units from dropdown
Specifications | Safety Valve Connection Size | N/A |  | Choose units from dropdown
Specifications | Condensate Drain Size | 1/2 | inches | Choose units from dropdown
Specifications | Flue Connection Size | 100 | mm
Specifications | Flue Connection Position | Internal | Enumeration | State whether external or internal
Specifications | Air Inlet Connection Size | 100 | mm
Specifications | Air Inlet Connection Position | Internal | Enumeration | State whether external or internal
Performance Data
Specifications | Sound Pressure Level | 62 | dBA | Measured at 1m from the casing
Specifications | Primary Fuel | Gas - LPG | Enumeration
Specifications | Optional Fuel | Gas - NG | Enumeration | If Not Applicable, choose 'No Optional Fuel'
Specifications | Gas Consumption rate | 8 | m³/h | If Not Applicable Mark '0'
Specifications | Oil Consumption rate | 0 | l/h | If Not Applicable Mark '0' DT
Specifications | Rated Output | 80.2 | kW | Product rated output
Specifications | Rated Criteria | Other | Enumeration | 10° differential on flow/return
Specifications | ErP Water Heating Energy Efficiency | 94 | % | Refer to Ecodesign Lot 1
Specifications | Primary Flow Rate | 108 | l/min | Refer to Ecodesign Lot 1
Specifications | Recovery Rate | 23 | l/min | State Recovery rate at 50ºC DT
Specifications | NOx Emissions | 39 | mg/kWh | NOx Emissions at 0% O2
Specifications | Hydraulic Resistance at 11C temperature differential | 607 | mbar | Hydraulic Resistance at 11ºC Δt
Specifications | Hydraulic Resistance at 20C temperature differential | NA | mbar | Hydraulic Resistance at 20ºC Δt
Specifications | Minimum Flow Rate at 11C temperature differential | 1.8 | l/s | Minimum flow rate at 11ºC Δt
Specifications | Minimum Flow Rate at 20C temperature differential | NA | l/s | Minimum flow rate at 20ºC Δt
Specifications | Maximum Operating Pressure | 11 | bar | Water side
Specifications | Minimum Operating Pressure | 0.5 | bar | Water side
Specifications | Nominal Gas Inlet Pressure | 37 | mbar | Standard gas inlet pressure. If Not Applicable Mark '0'
Specifications | Minimum Gas Inlet Pressure | 27 | mbar | Minimum safe gas inlet pressure. If Not Applicable Mark '0'
Specifications | Maximum Gas Inlet Pressure | 45 | mbar | Maximum safe gas inlet pressure. If Not Applicable Mark '0'
Specifications | Nominal Oil Inlet Pressure |  | mbar | Standard oil inlet pressure. If Not Applicable Mark '0'
Specifications | Minimum Oil Inlet Pressure |  | mbar | Minimum safe oil inlet pressure. If Not Applicable Mark '0'
Specifications | Maximum Oil Inlet Pressure |  | mbar | Maximum safe oil inlet pressure. If Not Applicable Mark '0'
Electrical Data
Specifications | Voltage | 230 | Volts
Specifications | Supply Phase | 1 | Number | 1,3
Specifications | Frequency | 50 | Hertz | eg. N/A, DC, 50,60, Other, UserDefined
Specifications | IP Rating | IP00 | Text | Ingress Protection rating e.g. IP56
Specifications | IK Rating | N/A | Text | Impact Resistance rating
Specifications | Starting Current | 0.78 | Amps
Specifications | Full Load Current | 0.78 | Amps
Specifications | Fuse Rating | 3 | Amps | At stated voltage
Specifications | Maximum Power Consumption | 180 | W
Specifications | Minimum Power Consumption | 180 | W
Controls
Specifications | Control Type | Internal control with high resolution interface | Text | Time control, night set back, cascade control
Specifications | BMS Links | Y | Y/N
Specifications | Interlocks | Y | Y/N
Sustainability
Sustainable Material BREEAM etc | Embodied Carbon |  | kgCO2e | Awaiting industry standard
Sustainable Material BREEAM etc | Life Cycle Analysis |  | Number | Awaiting industry standard
Sustainable Material BREEAM etc | Location of Manufacturer |  | GridRef | Awaiting industry standard
Sustainable Material BREEAM etc | Green Guide for Specification |  | Enumeration | A - E (Awaiting industry standard)
Sustainable Material BREEAM etc | Environmental Product Declaration |  | Text | 3rd Party Verification (Awaiting industry standard)
Sustainable Material BREEAM etc | Responsible Sourcing of Materials |  | Enumeration | Endorsing body (Awaiting industry standard)
Sustainable Material ETL | Energy Technology List | 0 | URL | Hyperlink to ETL webpage for product. If Not Applicable Mark '0'
Sustainable Material LEED v.4 | Responsible Extraction of Materials |  | Text | Awaiting industry standard
Sustainable Material LEED v.4 | Material Ingredient Reporting |  | Text | Awaiting industry standard
Sustainable Product Directive Ecodesign | ErP Energy Label | A | Text | State ErP efficiency class. If Not Applicable Mark '0'
Operations & Maintenance
Facilities/Asset Management | O&M Manual |  | URL | Hyperlink to Manufacturer O&M Data
Facilities/Asset Management | Daily |  | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Weekly |  | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Monthly |  | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Quarterly |  | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | 6 Monthly |  | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Annually | SERVICE | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Bespoke Timeframe |  | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 0-300hrs |  | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 301-600hrs |  | text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 601-1000hrs |  | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 1001-2000hrs |  | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 2001-4000hrs |  | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 4001-8000hrs |  | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 8001-12000hrs |  | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Expected Life | 20 YEARS | Years
Facilities/Asset Management | Warranty ID | 1 YEAR, 5 ON HEAT EXCHANGER | Text
This spreadsheet is the property of CIBSE although it can be freely used in the ways described, and completed with data specific to particular products. It is important that the Categories and Parameters given on the form are not changed. It is also important that where units of measurement are defined on the form that these too are followed. Any comment or suggestion on their revision should be addressed to pdt@cibse.org