## Water Heater - Continuous Flow
Template Category | Water Heater (Continuous Flow) - Gas
Template Version | v1
Category Description | Direct Fired Continuous Flow Water Heater used to produce potable hot water
Classification System
Classification | Value
Suitability for Use | Pending Approval
Template Custodian | CIBSE
Information Category | Parameter Name | Value | Units | Notes
Manufacturer Data
Specifications | Manufacturer | Lochinvar Limited | Text
Specifications | Manufacturer Website | www.lochinvar.ltd.uk | URL
Specifications | Product Range | Impetus | Text
Specifications | Product Model Number | IM750 | Text | Or Code
Specifications | CE Approval | Yes, KIP-15035/G | Text | Number, Yes, No
Specifications | Product Literature | http://lochinvar.ltd.uk/heater/ecoshield%E2%84%A2-water-heaters | URL
Specifications | Features | • Gross nominal input of 28.3kW (25.5kW net) • CE Certified with a Part L2 Seasonal Efficiency of 96 % • NOx emissions of no more than 20mg/kWh at 0% O2 • Capable of producing 464l/hr continuous at a 50°C temperature rise • 316 Ti Stainless steel heat exchanger with 2 pass Variable radiant circulation • Fully modulating burner with 8:1 turndown • 2 year parts warranty • 3 year warranty on heat exchanger • Integral control featuring as standard: o Water heater status | Text | Free text to describe product
Construction Data
Specifications | Type | Unset | Enumeration
Specifications | Shape | Rectangular (Vertical) | Enumeration
Specifications | External Material | Plastic | Enumeration
Specifications | Colour | White | Text | e.g. Colour(s) & RAL(s)
Specifications | Finish | Natural (self finish) | Text | e.g. Anodised, Brushed, Painted, Natural (Self-finish)
Specifications | Mounting | Internal Wall Mounted | Enumeration
Specifications | Burner Control Type | Modulating | Enumeration
Specifications | Primary Heat Exchanger Material | Stainless Steel | Enumeration
Specifications | Secondary Heat Exchanger Material | Stainless Steel | Enumeration | If not applicable, choose 'No Secondary Heat Exchanger'
Specifications | Fuel Connection Type | Threaded | Enumeration
Specifications | Supply Inlet Connection Type | Threaded | Enumeration
Specifications | Flow Connection Type | Threaded | Enumeration
Specifications | Drain Connection Type | Unset | Enumeration
Specifications | Safety Valve Connection Type | Threaded | Enumeration
Specifications | Condensate Drain Type | Plain | Enumeration | If Not Applicable, choose non-condensing
Specifications | Flue or Air Intake Classification | B23,C13,C33,C43,C53,C63,C83 | Text | Enter flue/air intake classification standard, e.g. 'B23'
Application Data
Specifications | Reference Standard | EN26:1997.EN26/A1:2000,EN26/A2:2004,EN26/A3:2006,EN26/AC:1998,EN677:1998 | Text | e.g BS/EN/ISO
Specifications | Approval | none | Text | WRAS Number
Dimensional Data
Specifications | Overall Length | 305 | mm | If Not Applicable Mark '0'
Specifications | Overall Width | 445 | mm | If Not Applicable Mark '0'
Specifications | Overall Diameter | 0 | mm | If Not Applicable Mark '0'
Specifications | Overall Height | 800 | mm
Specifications | Gross Weight | 38.9 | kg | Equates to Operating Weight
Specifications | Water Content | 2.9 | litres | Equates to Water Storage Capacity
Specifications | Shipping Weight | 37 | kg | Equates to dry weight of unit plus packaging allowance
Specifications | Access Clearance Top | 300 | mm | Access required for maintenance of this item
Specifications | Access Clearance Bottom | 300 | mm | Access required for maintenance of this item
Specifications | Access Clearance Left | 100 | mm | Access required for maintenance of this item
Specifications | Access Clearance Right | 100 | mm | Access required for maintenance of this item
Specifications | Access Clearance Front | 600 | mm | Access required for maintenance of this item
Specifications | Access Clearance Rear | 0 | mm | Access required for maintenance of this item
Specifications | Fuel Connection Size | 3/4 | inches | Choose units from dropdown
Specifications | Supply Inlet Connection Size | 3/4 | inches | Choose units from dropdown
Specifications | Flow Connection Size | 1 | inches | Choose units from dropdown
Specifications | Drain Connection Size | 0 |  | Choose units from dropdown
Specifications | Safety Valve Connection Size | 1/2 | inches | Choose units from dropdown.
Specifications | Condensate Drain Size | 20 | mm | Choose units from dropdown
Specifications | Flue Connection Size | 60 | mm | Choose units from dropdown
Specifications | Air Inlet Connection Size | 80 |  | Choose units from dropdown
Performance Data
Specifications | Sound Pressure Level | 61 | dBA | Measured at 1m from the casing
Specifications | Fuel Type | Gas - NG | Enumeration | Enter types of gas applicable
Specifications | Gas Flow Rate | 3.4 | m3/h | If Not Applicable Mark '0'
Specifications | Gross Heat Input | 35.5 | kW
Specifications | Thermal Efficiency | 95 | % | Refer to Gross CV in Building Regulations.
Specifications | ErP Load Profile | XXL | Enumeration | Refer to Declared Load Profile in Ecodesign Lot 2
Specifications | ErP Efficiency | 92 | % | Refer to Gross CV in Ecodesign Lot 2
Specifications | Maximum Water Temperature | 75 | °C
Specifications | Control thermostat range | 40-75 | °C | E.g. 30ºC - 80ºC
Specifications | Continuous output at 44 degree differential | 655 | l/h | State Continuous Output at 44°CΔt
Specifications | Continuous output at 50 degree differential | 576 | l/h | State Continous Output at 50°CΔt
Specifications | Continuous output at 35 degree differential | 822 | l/h | State Continous Output at 35°CΔt
Specifications | Emissions | 29 | mg/kWh | NOx Emissions at 0% O2
Specifications | Maximum Operating Pressure | 10 | bar | Maximum operating pressure when open vented
Specifications | Minimum Operating Pressure | 1 | bar | Minimum operating pressure
Specifications | Nominal Gas Inlet Pressure | 20 | mbar | Standard gas inlet pressure
Specifications | Minimum Gas Inlet Pressure | 15 | mbar | Minimum safe gas inlet pressure
Specifications | Maximum Gas Inlet Pressure | 45 | mbar | Maximum safe gas inlet pressure
Electrical Data
Specifications | Voltage | 230 | Volts
Specifications | Supply Phase | 1 | Number | 1,3
Specifications | Frequency | 50 | Hertz | eg. N/A, DC, 50,60, Other, UserDefined
Specifications | IP Rating | IPX4D | Text | Ingress Protection rating e.g. IP56
Specifications | IK Rating | N/A | Text | Impact Resistance rating
Specifications | Starting Current | 0.70 | Amps
Specifications | Full Load Current | 0.70 | Amps
Specifications | Fuse Rating | 5 | Amps | At stated voltage
Specifications | Maximum Power Consumption | 162 | W
Controls
Specifications | Control Type | Modulating | Text | Free text to describe controls
Specifications | BMS Links | N | Y/N
Specifications | Interlocks | N | Y/N
Sustainability
Sustainable Material BREEAM etc | Embodied Carbon |  | kgCO2e | University of Bath ICE Data if none other available (Awaiting industry standard)
Sustainable Material BREEAM etc | Life Cycle Analysis |  | Number | BREEAM (Awaiting industry standard)
Sustainable Material BREEAM etc | Location of Manufacturer |  | GridRef | Northing, Easting (Awaiting industry standard)
Sustainable Material BREEAM etc | Green Guide for Specification |  | Enumeration | A - E (Awaiting industry standard)
Sustainable Material BREEAM etc | Environmental Product Declaration |  | Text | 3rd Party Verification (Awaiting industry standard)
Sustainable Material BREEAM etc | Responsible Sourcing of Materials |  | Enumeration | Endorsing body (Awaiting industry standard)
Sustainable Material ETL | Energy Technology List | 0 | URL | Hyperlink to ETL webpage for product. If Not Applicable Mark '0'
Sustainable Material LEED v.4 | Responsible Extraction of Materials |  | Text | (Awaiting industry standard)
Sustainable Material LEED v.4 | Material Ingredient Reporting |  | Text | (Awaiting industry standard)
Sustainable Product Directive Ecodesign | ErP Energy Label | Y | Y/N
Operations & Maintenance
Facilities/Asset Management | Operation and Maintenance Manual | http://lochinvar.ltd.uk/heater/ecoshield%E2%84%A2-water-heaters | URL | Hyperlink to Manufacturer O&M Data
Facilities/Asset Management | Daily | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Weekly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Monthly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Quarterly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | 6 Monthly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Annually | Full Service | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Bespoke Timeframe | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Expected Life | 20 | Years
Facilities/Asset Management | Warranty ID | 3 year heat exchanger, 2 year all other parts | Text
This spreadsheet is the property of CIBSE although it can be freely used in the ways described, and completed with data specific to particular products. It is important that the Categories and Parameters given on the form are not changed. It is also important that where units of measurement are defined on the form that these too are followed. Any comment or suggestion on their revision should be addressed to pdt@cibse.org