## Water Heater Storage
Template Category | Water Heater (Storage) - Gas or Oil
Template Version | v1
Category Description | Direct Fired Gas & Oil, Storage Water Heater used to produce hot water
Classification System
Classification | Value
Suitability for Use | Approved
Template Custodian | CIBSE
Information Category | Parameter Name | Value | Units | Notes
Manufacturer Data
Specifications | Manufacturer | Lochinvar Limited | Text
Specifications | Manufacturer Website | www.lochinvar.ltd.uk | URL
Specifications | Product Range | EcoShield | Text
Specifications | Product Model Number | SHW116-410CE | Text | Or Code
Specifications | CE Approval | Yes, 85931/01 | Text | Number, Yes, No
Specifications | WRAS Approval | No | Text | Number, Yes, No
Specifications | Product Literature | http://lochinvar.ltd.uk/heater/ecoshield%E2%84%A2-water-heaters | URL
Specifications | Features | Fully Modulating burner 5:1 turndown, stainless steel heat exchanger, inegral A rated pump | Text | Free text to describe product
Construction Data
Specifications | Type | Direct fired hot water generation | Enumeration
Specifications | Shape | Cylindrical (Vertical) | Enumeration
Specifications | External Material | Steel | Enumeration
Specifications | Colour | Grey | Text | e.g. Colour(s) & RAL(s)
Specifications | Finish | Paint | Text | e.g. Anodised, Brushed, Painted, Natural (Self-finish)
Specifications | Mounting | Floor Standing | Enumeration
Specifications | Heater Operation | Fully condensing | Enumeration | State whether product has condensing function
Specifications | Heat Exchanger Material | Stainless Steel | Enumeration
Specifications | Fuel Connection Type | Threaded | Enumeration
Specifications | Flow and Return Connection Type | Threaded | Enumeration
Specifications | Secondary Return Connection Type | Unset | Enumeration
Specifications | Drain Connection Type | Threaded | Enumeration
Specifications | Safety Valve Connection Type | Threaded | Enumeration
Specifications | Condensate Drain Connection Type | Other | Enumeration
Specifications | Clean Out Cover and Inspection Opening Type | Flanged | Enumeration
Specifications | Flue or Air Intake Classification | B23,C13,C33,C43,C53,C63 | Text | Enter flue/air intake classification standard, e.g. 'B23'
Application Data
Specifications | Reference Standard | EN89-2000 | Text | BS, EN, ISO
Dimensional Data
Specifications | Overall Length | 865 | mm | Depth or Diameter
Specifications | Overall Width | 0 | mm | If Not Applicable Mark '0'
Specifications | Overall Height | 1920 | mm
Specifications | Gross Weight | 838 | kg | Equates to Operating Weight
Specifications | Water Content | 423 | litres | Equates to Water Storage Capacity
Specifications | Shipping Weight | 388 | kg | Equates to dry weight of unit plus packaging allowance
Specifications | Access Clearance Top | 450 | mm | Access required for maintenance of this item
Specifications | Access Clearance Bottom | 0 | mm | Access required for maintenance of this item
Specifications | Access Clearance Left | 600 | mm | Access required for maintenance of this item
Specifications | Access Clearance Right | 100 | mm | Access required for maintenance of this item
Specifications | Access Clearance Front | 600 | mm | Access required for maintenance of this item
Specifications | Access Clearance Rear | 0 | mm | Access required for maintenance of this item
Specifications | Fuel Connection Size | 1 | inches | Choose units from dropdown
Specifications | Flow and Return Connection Size | 2 | inches | Choose units from dropdown
Specifications | Secondary Return Connection Size | 0 | inches | Choose units from dropdown
Specifications | Drain Connection Size | 3/4 | inches | Choose units from dropdown
Specifications | Safety Valve Connection Size | 1 | inches | Choose units from dropdown
Specifications | Condensate Drain Size | 3/4 | inches | Choose units from dropdown. If Not Applicable Mark '0'
Specifications | Clean Out Cover and Inspection Opening Size | Flanged | inches | Choose units from dropdown
Specifications | Flue Connection Size | 100 | mm | Also state whether internal or external
Specifications | Air Inlet Connection Size | 100 | mm | Also state whether internal or external
Performance Data
Specifications | Sound Pressure Level | 62 | dBA | Measured at 1m from the casing
Specifications | Fuel Type | Gas - NG | Enumeration | Type of fuel used
Specifications | Gas Consumption rate | 11.1 | m3/h | If Not Applicable Mark '0'
Specifications | Oil Consumption rate | 0 | l/h | If Not Applicable Mark '0'
Specifications | Gross Input | 116.9 | kW
Specifications | Heat Generator Thermal Efficiency | 94.6 | % | Refer to Gross CV in Building Regulations.
Specifications | Heat Generator Load Profile | 3XL | Enumeration | Refer to Declared Load Profile in Ecodesign Lot 2
Specifications | Heat Generator Efficiency | 78 | % | Refer to Gross CV in Ecodesign Lot 2
Specifications | Maximum Water Temperature | 80 | °C | Maximum stored water temperature
Specifications | Control thermostat range | 16-85 | °C | e.g. 10-95ºC
Specifications | Recovery Rate | 31.7 | litre/min | State Recovery rate at 10-60ºC
Specifications | Continuous output at 44 degree differential | 2164 | l/h | State Continuous Output at 44°CΔt
Specifications | Continuous output at 50 degree differential | 1904 | l/h | State Continuous Output at 50°CΔt
Specifications | Heat up time | 13 | mins | State Heat up time from 10-60ºC
Specifications | Standing Loss | 114 | W | Refer to Standing Loss in Ecodesign Lot 2
Specifications | Water Treatment Required | Y | Y/N | State whether product requires water treatment. If yes, refer to manufacturer's instructions.
Specifications | NOx Emissions | 61.6 | mg/kWh | At 0% O2
Specifications | Insulation Type | Polyurethane | Text | State integral thermal insulation type
Specifications | Insulation Thickness | 50 | mm
Specifications | Maximum Operating Pressure when Open Vented | 11 | bar | Water side
Specifications | Maximum Operating Pressure when Unvented | 11 | bar | Water side
Specifications | Minimum Operating Pressure | 1 | bar | Water side
Specifications | Nominal Gas Inlet Pressure | 20 | mbar | Standard gas inlet pressure
Specifications | Minimum Gas Inlet Pressure | 17.5 | mbar | Minimum safe gas inlet pressure
Specifications | Maximum Gas Inlet Pressure | 25 | mbar | Maximum safe gas inlet pressure
Specifications | Nominal Oil Inlet Pressure |  | mbar | Standard oil inlet pressure
Specifications | Minimum Oil Inlet Pressure |  | mbar | Minimum safe oil inlet pressure
Specifications | Maximum Oil Inlet Pressure |  | mbar | Maximum safe oil inlet pressure
Electrical Data
Specifications | Voltage | 230 | Volts
Specifications | Supply Phase | 1 | Number | 1,3
Specifications | Frequency | 50 | Hertz | eg. N/A, DC, 50,60, Other, UserDefined
Specifications | IP Rating | IP00 | Text | Ingress Protection rating e.g. IP56
Specifications | IK Rating | N/A | Text | Impact Resistance rating
Specifications | Starting Current | 4.0 | Amps
Specifications | Full Load Current | 4.0 | Amps
Specifications | Fuse Rating | 10 | Amps | At stated voltage
Specifications | Maximum Power Consumption | 932 | W
Specifications | Minimum Power Consumption | 0 | W
Controls
Specifications | Control Type | Internal | Enumeration | State whether controls are internal or external
Specifications | BMS Links | Y | Y/N
Specifications | Control Options | Modulating | Enumeration
Specifications | Interlocks | Y | Y/N
Sustainability
Sustainable Material BREEAM etc | Embodied Carbon |  | kgCO2e | Awaiting industry standard
Sustainable Material BREEAM etc | Life Cycle Analysis |  | Number | Awaiting industry standard
Sustainable Material BREEAM etc | Location of Manufacturer |  | GridRef | Awaiting industry standard
Sustainable Material BREEAM etc | Green Guide for Specification |  | Enumeration | Awaiting industry standard
Sustainable Material BREEAM etc | Environmental Product Declaration |  | Text | 3rd Party Verification
Sustainable Material BREEAM etc | Responsible Sourcing of Materials |  | Enumeration | (Awaiting industry standard)
Sustainable Material ETL | Energy Technology List | 0 | URL | Hyperlink to ETL webpage for product. If Not Applicable Mark '0'
Sustainable Material LEED v.4 | Responsible Extraction of Materials |  | Text | Awaiting industry standard
Sustainable Material LEED v.4 | Material Ingredient Reporting |  | Text | Awaiting industry standard
Sustainable Product Directive Ecodesign | ErP Energy Label | B | Text | State ErP efficiency class. If Not Applicable Mark '0'
Operations & Maintenance
Facilities/Asset Management | O&M Manual | http://lochinvar.ltd.uk/heater/ecoshield%E2%84%A2-water-heaters | URL | Hyperlink to Manufacturer O&M Data
Facilities/Asset Management | Daily | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Weekly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Monthly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Quarterly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | 6 Monthly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Annually | Full service | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Bespoke Timeframe | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 0-300hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 301-600hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 601-1000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 1001-2000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 2001-4000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 4001-8000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 8001-12000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Expected Life | 20 | Years
Facilities/Asset Management | Warranty ID | 5year warranty tank and heat exchanger, 12 months parts | Text
This spreadsheet is the property of CIBSE although it can be freely used in the ways described, and completed with data specific to particular products. It is important that the Categories and Parameters given on the form are not changed. It is also important that where units of measurement are defined on the form that these too are followed. Any comment or suggestion on their revision should be addressed to pdt@cibse.org